## Slide 1
Operational research for urban solar development
“PV failure detection based on operational time series”
Alexandre Mathieu
13/11/2023 - Morning

## Slide 2: Agenda
Curriculum
Audience
PV performance model steps

## Slide 3: Curriculum
Day | Time | Duration | Content
Monday 13/11/2023 | 8h-9h30 9h45-11h15 | 1h30 + 1h30 | 50% Lecture / 50 % Hands-on
Monday 27/11/2023 | 9h45-11h15 12h30-14h | 1h30 + 1h30 | 50% Lecture / 50 % Hands-on
Friday 01/12/2023 | 8h-11h 13h15-16h15 | 6h | 25% Lecture / 75 % Hands-on / Project
Thursday 07/12/2023 | 8h-11h 12h45-15h45 | 6h | 10% Lecture / 90 % Project
Friday 22/12/2023 | 8h-9h30 | 1h30 | 100 % Project
Initial plan

## Slide 4: Curriculum
Content
PV performance modeling from weather variables (Irradiance in the plane of array, ambient temperature etc..) and system configuration, which includes:
  Module temperature
  DC power
  AC/DC efficiency
  Performance metric calculations.
Failure detection based on real production time series.
Hands-on with python notebooks.

## Slide 5: Curriculum
Motivations
15%[4] of underperformances: « Recoverable » Energy: 5%[4,5]
Complex in-situ O & M: No one-fit-all O&M[2] Expensive[3]
PV capacity increases exponentially
+20%/year worldwide since 2010[1]
[1] Masson, G., Kaizuka, I., 2021. Trends in Photovoltaic Applications (IEA-PVPS T1-41:2021). IEA PVPS
[2] U. Jahn et al., ‘Guidelines for Operation and Maintenance of Photovoltaic Power Plants in Different Climates’, IEA, Technical Report IEA-PVPS T13-07:2022, Oct. 2022. [3] « Coûts et rentabilités du grand photovoltaïque en métropole continentale », CRE, 2019
[4] Leloux, J., Narvarte, L., Trebosc, D., 2011. Performance analysis of 10,000 residential PV systems in France and Belgium. Presented at the 26th European Photovoltaic Solar Energy Conference and Exhibition, Hamburg, Germany.) [5] Raycatch, ‘Solar Asset Optimization, Industry Benchmark Study’, Tel Aviv, Israel, Feb. 2021.

## Slide 6: Curriculum
Objectives
At the end of this course, you should be able to:
Perform data treatment and analysis with Python on operational PV time series.
Model and calculate the performance of a PV installation.
Detect and quantify underperformances.

## Slide 7
Audience

## Slide 8: Audience
You
Background
PV modeling
Python
Notes: Where do you come from ? Education
Expérience with python and PV modeling

## Slide 9: Agenda
Curriculum
Audience
PV performance model steps

## Slide 10: Modeling steps
*image from: PVSC48 python tutorial

## Slide 11: Modeling steps
Weather data: Irradiance, ambient temperature, humidity, rain, snow…

## Slide 12: Modeling steps
Weather data:
Irradiance, measured in W/m2, with max instantaneous values around 1000 W/m2 is obtained from:
  Satellite data (CAMS, NSSRDB, SolarGis…)
Some Irradiance datasets, supported by pvlib [1]
[1] Adam R. Jensen, Kevin S. Anderson, William F. Holmgren, Mark A. Mikofski, Clifford W. Hansen, Leland J. Boeman, Roel Loonen,
pvlib iotools—Open-source Python functions for seamless access to solar irradiance data, Solar Energy, 2023

## Slide 13: Modeling steps
Weather data:
Irradiance, measured in W/m2, is obtained from:
  Satellite data (CAMS, NSSRDB, SolarGis…)
  In-situ instrumentations
Pyranometer: Global/Inclined Irradiance
Pyranometer with shadow ring: Diffuse Irradiance
Pyrheliometer: Direct irradiance
(Hukseflux product)

## Slide 14: Modeling steps
Weather data:
Irradiance, measured in W/m2, is obtained from:
  Satellite data (CAMS, NSSRDB, SolarGis…)
  In-situ instrumentations
Reference cell: Inclined Irradiance (without reflection/spectral effects)

## Slide 15: Modeling steps
Weather data
Reminder, the Global Horizontal Irradiance (GHI) can be broken down into 2 components (ignoring reflections from other surrounding elements):
(Beam Horizontal Irradiance): Power received from the Beam of the sun on the horizontal plan.
(Diffuse Horizontal Irradiance): Power received from the sky diffusion of the light.
*image from PVSC48 tutorial

## Slide 16: Modeling steps
Weather data
Reminder, the Global Horizontal Irradiance (GHI) can be broken down into 2 components (ignoring reflections from other surrounding elements):
(Beam Horizontal Irradiance): Power received from the Beam of the sun on the horizontal plan. BHI is usually deducted from DNI, the Direct Normal Irradiance, which is most commonly the output of weather models.
(Diffuse Horizontal Irradiance): Power received from the sky diffusion of the light.
the zenith angle
*image adapted from PVSC48 tutorial

## Slide 17: Modeling steps
Weather data:
Sun path
Image: https://www.prairielittlebighouse.com/prairie-blog/archives/03-2021
z
Φ

## Slide 18: Modeling steps
Weather data:
The sun path is characterized by:
z [°], elevation angle, height of the sun in the sky
z
Φ
*animation from pveducation

## Slide 19: Modeling steps
Weather data:
The sun path is characterized by:
z [°], elevation angle, height of the sun in the sky
Φ [°], the azimuth angle: angle of sun between north and sun direction
z
Φ
*animation from pveducation
*animation from pveducation

## Slide 20: Modeling steps
Weather data:
The sun path is characterized by:
z [°], elevation angle, height of the sun in the sky
Φ [°], the azimuth angle: angle between north and the sun direction
Φ [°]
z [°]
Typical sun path diagram

## Slide 21: Modeling steps
Weather data:
The sun path is characterized by:
z [°], elevation angle, height of the sun in the sky
Φ [°], the azimuth angle: angle between north and the sun direction
Remember ? To calculate BHI:
z
Φ
With , the zenith angle
the zenith angle
*image adapted from PVSC48 tutorial

## Slide 22: Modeling steps
2. Plan-of-Array Irradiance
Reminder, the Global Plane-Of-Array (GPOA) irradiance can be calculated from DHI, GHI and DNI.

## Slide 23: Modeling steps
2. Plan-of-Array Irradiance
Reminder, the Global Plane-Of-Array (GPOA) irradiance can be calculated from DHI, GHI and DNI and are broken down into 3 components:
Souza, Muriele et al. (2019). Determination of Diffused Irradiation from Horizontal Global Irradiation - Study for the City of Curitiba.
: The direct component - Power received from the Beam of the sun on the horizontal plan
: The ground-reflected component - Power received from reflections from the ground
: The diffuse component - Power received from the sky diffusion of the light,

## Slide 24: Modeling steps
Souza, Muriele et al. (2019). Determination of Diffused Irradiation from Horizontal Global Irradiation - Study for the City of Curitiba.
Under the isotropic/no-shading assumption
2. Plan-of-Array Irradiance
Reminder, the Global Plane-Of-Array (GPOA) irradiance can be calculated from DHI, GHI and DNI and are broken down into 3 components:
With:
, PV installation tilt

## Slide 25: Modeling steps
=
With:
AOI, angle of incidence
, PV installation tilt
, PV installation azimuth
Sun elevation
, sun azimuth
Under the isotropic/no-shading assumption
2. Plan-of-Array Irradiance
Reminder, the Global Plane-Of-Array (GPOA) irradiance can be calculated from DHI, GHI and DNI and are broken down into 3 components:

## Slide 26: Modeling steps
2. Plan-of-Array Irradiance
Use the notebook: https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy/blob/master/notebooks/python_intro_poa.ipynb
Follow the python tutorial and calculate the 3 POA components for:
One timestep
Over one year
Time for some hands-on exercises

## Slide 27: Modeling steps
3. Shading
Shadow can come from near and far elements and their impact can be distinguished into two categories
Partial shading refers to a condition where some but not all of the solar cells or panels in a PV array are exposed to sunlight while others are shaded.
Full shading occurs when the entire PV array is covered and deprived of direct sunlight.
*https://mcisolutions.ca/effect-of-shade-on-solar-panels/

## Slide 28: Modeling steps
Not treated in this course but, in average, if a PV panel is around 8% covered, the whole PV panel is bypassed and then, do not produce.
3. Shading
Shadow can come from near and far elements and their impact can be distinguished into two categories
Partial shading refers to a condition where some but not all of the solar cells or panels in a PV array are exposed to sunlight while others are shaded.
Full shading occurs when the entire PV array is covered and deprived of direct sunlight.
*https://mcisolutions.ca/effect-of-shade-on-solar-panels/
Demonstrated in one of pvlib example: https://pvlib-python.readthedocs.io/en/stable/gallery/shading/plot_partial_module_shading_simple.html

## Slide 29: Modeling steps
3. Shading
The Fisheye camera enables to account for the in-situ (full) shading in PV modeling.
Example in South of France
East
South
West
North
Fisheye camera

## Slide 30: Modeling steps
3. Shading
The Fisheye camera enables to account for the in-situ (full) shading in PV modeling.
Fisheye camera
Example in South of France
East
South
West
North

## Slide 31: Modeling steps
3. Shading
The Fisheye camera enables to account for the in-situ (full) shading in PV modeling.
Under the black curve, simple assumptions lead to:
are not significantly modified
Example in South of France
East
South
West
North

## Slide 32: Modeling steps
3. Soiling losses
Big subject in the PV industry:
Report of 130 pages on PV soiling: IEA PVPS, Soiling Losses – Impact on the Performance of Photovoltaic Power Plants 2022

## Slide 33: Modeling steps
3. Soiling losses
Can roughly be ignored in France according to the HSU model.
Model HSU: M. Coello and L. Boyle, "Simple Model for Predicting Time Series Soiling of Photovoltaic Panels, Sept. 2019.

## Slide 34: Modeling steps
3. Shading / Terrain horizon mask
Time for some hands-on exercises,
Again!

## Slide 35: Modeling steps
3. Shading / Terrain horizon mask
PVGIS: Website/Online Tool to estimate power production:
Enables to extract the horizon mask with a Digital Surface Model (DSM).
Go to: https://re.jrc.ec.europa.eu/pvg_tools/en/
Time for some hands-on exercise's,
Again !

## Slide 36: Modeling steps
3. Shading / Terrain horizon mask
PVGIS: Website/Online Tool to estimate power production: https://re.jrc.ec.europa.eu/pvg_tools/en/
Enables to extract the horizon mask with a Digital Surface Model (DSM).
Instructions:
Generate a simulation on PVGIS
  Click on the map on Grenoble and select the « Grid connected tab »
  Vizualize
  Extract the horizon file in csv format
2. Follow the instructions on the jupyter notebook and calculate the modified POA on one year. https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy/blob/master/notebooks/python_intro2_horizon_mask.ipynb
Notes: Show function
Create function to get the API horizon mask
How many hours is the direct component blocked ?

## Slide 37: Modeling steps
4. Module and Cell temperature
The hotter a module is, the less efficient it is !

## Slide 38: Modeling steps
4. Cell temperature
Ross model: Model to estimate the cell temperature [°C] as function of ambient temperature and irradiance [W/m²].
, typically in the range 0.02-0.05 K/m²/W.
Ross, R. G. Jr., (1981). “Design Techniques for Flat-Plate Photovoltaic Arrays”

## Slide 39: Modeling steps
4. Cell temperature
Ross model: Model to estimate the cell temperature [°C] as function of ambient temperature and irradiance [W/m²].
, typically in the range 0.02-0.05 K/m²/W.
can be fitted from datasheet values. NOCT conditions: = 800 W/m²
= 20°C
Ross, R. G. Jr., (1981). “Design Techniques for Flat-Plate Photovoltaic Arrays”

## Slide 40: Modeling steps
4. Cell temperature
Faiman model: Model to estimate the cell temperature [°C] as function of ambient temperature and irradiance [W/m²] AND wind .
Faiman, D. (2008). Assessing the outdoor operating temperature of photovoltaic modules.

## Slide 41: Modeling steps
4. Cell temperature
Faiman model: Model to estimate the cell temperature [°C] as function of ambient temperature and irradiance [W/m²] AND wind .
In some cases, can be assumed Between , only few degrees of difference
Faiman, D. (2008). Assessing the outdoor operating temperature of photovoltaic modules.

## Slide 42: Modeling steps
4. Cell temperature
Use the following notebook: https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy/blob/master/notebooks/dc_power_estimation.ipynb
Follow the python tutorial and estimate the cell temperature for one year.
Time for some hands-on exercises !

## Slide 43: Modeling steps
5. Module and String IV Curve

## Slide 44: Modeling steps
5. Module and String IV Curve
For a fixed irradiance and module temperature, the PV module has its I, current which depends on V, voltage and it can take many operating points.

## Slide 45: Modeling steps
In reality, the IV characteristics go out of the 1st quadrant and the module can potentially consume power.
5. Module and String IV Curve
For a fixed irradiance and module temperature, the PV module has its I, current which depends on V, voltage and it can take many operating points

## Slide 46: Modeling steps
5. Module and String IV Curve
For a fixed irradiance and module temperature, the PV module has its I, current which depends on V, voltage and it can take many operating points
Then, the inverter is constantly searching for the operating. point which maximizes the power MPP: Maximum Power Point.

## Slide 47: Modeling steps
5. Module and String IV Curve
For a fixed irradiance and module temperature, the PV module has its I, current which depends on V, voltage and it can take many operating points.
Then, the inverter is constantly searching for the operating. point which maximizes the power MPP: Maximum Power Point.
Especially, it changes the voltage with the MPP-Tracker (MPPT) to maximize power.

## Slide 48: Modeling steps
5. Module and String IV Curve
By the way… the IV curves can be summed up when the modules are connected in series or parallel! The inverter, then, maximizes the power of the PV array IV curve.
Bun, L.. “Détection et localisation de défauts pour un système PV.” (2011).

## Slide 49: Modeling steps
5. Module and String IV Curve
The IV curves' dependencies:
Higher cell temperatures mostly decrease the voltage
Higher irradiance level mostly increase the current
Example of I-V curves as function of different module temperature
Example of I-V curves as function of different irradiances

## Slide 50: Modeling steps
6. DC & Mismatch Losses
Not the focus of this class. However, keep in mind that:
DC wiring losses are around 0.5%-2%.
Mismatch losses refer to the fact that PV modules have different IV curves and this can entail significant losses.

## Slide 51: Modeling steps
6. DC & Mismatch Losses
Not the focus of this class. However, keep in mind that:
DC wiring losses are around between 0.5% and 2%.
Mismatch losses refers to the fact that PV modules have different IV curves and this can entail significant losses. For instance, if one of them has a very degraded IV curve (shading or other), it can significantly degrade the IV curve at the array level.
Bun, L.. “Détection et localisation de défauts pour un système PV.” (2011).

## Slide 52: Modeling steps
5./6./7. Power model
Constant efficiency model:
With:
, DC power in [W]
efficiency around 20% (from datasheet)
the irradiance in the plane of array [W/m²]
, the PV installation area [m2]

## Slide 53: Modeling steps
5./6./7. Power model
Constant efficiency model:
With:
, DC power in [W]
efficiency around 20% (from datasheet)
the irradiance in the plane of array [W/m²]
, the PV installation area [m2]
Not really precise for instantaneous values

## Slide 54: Modeling steps
5./6./7. Power model
The PVWatts model enables to take into account the effect of the cell temperature
With:
, the reference efficiency (around 20%) [%]
the irradiance in the plane of array [W/m²]
, the PV installation area [m2]
(negative, usually between -0.2 – -0.5 % W/m²/°C)
, the cell temperature [°C]
PVWatts model: A. P. Dobos, “PVWatts Version 5 Manual” (2014).

## Slide 55: Modeling steps
5./6./7. Power model
The Huld model (used in PVGIS) enables to take into account the module temperature and non-lineary with irradiance.
With:
, the reference efficiency (around 20%) [%]
the irradiance in the plane of array [W/m²]
, the PV installation area [m2]
the normalized irradiance
, the module temperature delta [°C]
coefficients
Huld model: Thomas Huld et al., A power-rating model for crystalline silicon PV modules, 2011,

## Slide 56: Modeling steps
5./6./7. Power model
The Huld model (used in PVGIS) enables to take into account the module temperature and non-lineary with irradiance.
With:
, the reference efficiency (around 20%) [%]
the irradiance in the plane of array [W/m²]
, the PV installation area [m2]
the normalized irradiance
, the module temperature delta [°C]
coefficients
Reference values from PVGIS
Huld model: Thomas Huld et al., A power-rating model for crystalline silicon PV modules, 2011,

## Slide 57: Modeling steps
5./6./7. Power model
Use the following notebook: https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy/blob/master/notebooks/dc_power_estimation.ipynb
Follow the python tutorial and estimate the DC power for one year.
Time for some hands-on exercises !

## Slide 58: Resources
Modeling guide PVPMC: https://pvpmc.sandia.gov/modeling-guide/
Python / Pvlib tutorial: https://pvsc-python-tutorials.github.io/PVSC48-Python-Tutorial/
To go further:
  The Use of Advanced Algorithms in PV Failure Monitoring: https://iea-pvps.org/wp-content/uploads/2021/10/Final-Report-IEA-PVPS-T13-19_2021_PV-Failure-Monitoring.pdf

## Slide 59: Appendix
How to install Python and import the course repository to use the notebooks on your local PC.
Install python: www.python.org/downloads/, download and install the 3.9.13 “release” (Add python to your Path)
Go to https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy, click on the green “Code” button and then download the folder as the zip

## Slide 60: Appendix
How to install Python and import the course repository to use the notebooks on your local PC.
Install python: www.python.org/downloads/, download and install the 3.9.13 “release” (Add python to your Path)
Go to https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy, click on the green “Code” button and then download the folder as the zip
Unzip it and put it in adequate location in your PC.
Let’s create a virtual environment where you will find all the functions for this course:
  Go in the folder and open the command line from that same folder by writing “cmd” in the path bar (with Windows)

## Slide 61: Appendix
How to install Python and import the course repository to use the notebooks on your local PC.
Install python: www.python.org/downloads/, download and install the 3.9.13 “release” (Add python to your Path)
Go to https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy, click on the green “Code” button and then download the folder as the zip
Unzip it and put it in adequate location in your PC.
Let’s create a virtual environment where you will find all the functions for this course:
  Go in the folder and open the command line from that same folder by writing “cmd” in the path bar (with Windows)
  In the command bar: execute the following line to create the “solar_env” environnement, you will use in your notebooks
    “pip install virtualenv”
    “python –m virtualenv solar_env”
    “call solar_env\Scripts\activate” (you should have a ‘solar_env’ on the left of the commande at this point)
    “pip install –r requirements.txt” (load all the libraries, take a little time, be patient)
    “python -m ipykernel install --name=solarkernel” (create a kernel for the notebooks)
It’s ready !

## Slide 62: Appendix
How to start a notebook
Go in the folder and open the command line from that same folder by writing “cmd” in the path bar (with Windows)
In the command bar, exexute:
  “call solar_env\Scripts\activate” (go in the virtual env)
  “jupyter notebook” (open the notebooks browser)
3. Browse to the notebooks folder, choose one and pick the solarkernel when asked.