## Slide 1
Operational research for urban solar development
“PV failure detection based on operational time series”
Alexandre Mathieu
27/11/2023 - Morning

## Slide 2: Agenda
Curriculum
Audience
PV performance model steps

## Slide 3: Curriculum
Day | Time | Duration | Content
Monday 27/11/2023 | 9h45-11h15 12h30-14h | 1h30 + 1h30 | 50% Lecture / 50 % Hands-on
Tuesday 05/12/2023 | 8h-9h30 9h45-11h15 | 1h30 + 1h30 | 50% Lecture / 50 % Hands-on
Thursday 07/12/2023 | 8h-11h 12h45-15h45 | 6h | 25% Lecture / 75 % Project
Monday 11/11/2023 | 8h-11h 12h30-15h30 | 6h | 10% Lecture / 90 % Project
Friday 22/12/2023 | 8h-9h30 | 1h30 | 100 % Project
Initial plan

## Slide 4: Curriculum
Content
PV performance modeling from weather variables (Irradiance in the plane of array, ambient temperature etc..) and system configuration, which includes:
  Module temperature
  DC power
  AC/DC efficiency
  Performance metric calculations.
Failure detection based on real production time series.
Hands-on with python notebooks.

## Slide 5: Curriculum
Motivations
15%[4] of underperformances: « Recoverable » Energy: 5%[4,5]
Complex in-situ O & M: No one-fit-all O&M[2] Expensive[3]
PV capacity increases exponentially
+20%/year worldwide since 2010[1]
[1] Masson, G., Kaizuka, I., 2021. Trends in Photovoltaic Applications (IEA-PVPS T1-41:2021). IEA PVPS
[2] U. Jahn et al., ‘Guidelines for Operation and Maintenance of Photovoltaic Power Plants in Different Climates’, IEA, Technical Report IEA-PVPS T13-07:2022, Oct. 2022. [3] « Coûts et rentabilités du grand photovoltaïque en métropole continentale », CRE, 2019
[4] Leloux, J., Narvarte, L., Trebosc, D., 2011. Performance analysis of 10,000 residential PV systems in France and Belgium. Presented at the 26th European Photovoltaic Solar Energy Conference and Exhibition, Hamburg, Germany.) [5] Raycatch, ‘Solar Asset Optimization, Industry Benchmark Study’, Tel Aviv, Israel, Feb. 2021.

## Slide 6: Curriculum
Objectives
At the end of this course, you should be able to:
Perform data treatment and analysis with Python on operational PV time series.
Model and calculate the performance of a PV installation.
Detect and quantify underperformances.

## Slide 7
Audience

## Slide 8: Audience
You
Background
PV modeling
Python
Notes: Where do you come from ? Education
Expérience with python and PV modeling

## Slide 9: Agenda
Curriculum
Audience
PV performance model steps

## Slide 10: Modeling steps
*image from: PVSC48 python tutorial

## Slide 11: Modeling steps
Weather data: Irradiance, ambient temperature, humidity, rain, snow…

## Slide 12: Modeling steps
Weather data:
Irradiance, measured in W/m2, with max instantaneous values around 1000 W/m2 is obtained from:
  Satellite data (CAMS, NSSRDB, SolarGis…)
Some Irradiance datasets, supported by pvlib [1]
[1] Adam R. Jensen, Kevin S. Anderson, William F. Holmgren, Mark A. Mikofski, Clifford W. Hansen, Leland J. Boeman, Roel Loonen,
pvlib iotools—Open-source Python functions for seamless access to solar irradiance data, Solar Energy, 2023

## Slide 13: Modeling steps
Weather data:
Irradiance, measured in W/m2, is obtained from:
  Satellite data (CAMS, NSSRDB, SolarGis…)
  In-situ instrumentations
Pyranometer: Global/Inclined Irradiance
Pyranometer with shadow ring: Diffuse Irradiance
Pyrheliometer: Direct irradiance
(Hukseflux product)

## Slide 14: Modeling steps
Weather data:
Irradiance, measured in W/m2, is obtained from:
  Satellite data (CAMS, NSSRDB, SolarGis…)
  In-situ instrumentations
Reference cell: Inclined Irradiance (without reflection/spectral effects)

## Slide 15: Modeling steps
Weather data
Reminder, the Global Horizontal Irradiance (GHI) can be broken down into 2 components (ignoring reflections from other surrounding elements):
(Beam Horizontal Irradiance): Power received from the Beam of the sun on the horizontal plan.
(Diffuse Horizontal Irradiance): Power received from the sky diffusion of the light.
*image from PVSC48 tutorial

## Slide 16: Modeling steps
Weather data
Reminder, the Global Horizontal Irradiance (GHI) can be broken down into 2 components (ignoring reflections from other surrounding elements):
(Beam Horizontal Irradiance): Power received from the Beam of the sun on the horizontal plan. BHI is usually deducted from DNI, the Direct Normal Irradiance, which is most commonly the output of weather models.
(Diffuse Horizontal Irradiance): Power received from the sky diffusion of the light.
the zenith angle
*image adapted from PVSC48 tutorial

## Slide 17: Modeling steps
Weather data:
Sun path
Image: https://www.prairielittlebighouse.com/prairie-blog/archives/03-2021
z
Φ

## Slide 18: Modeling steps
Weather data:
The sun path is characterized by:
z [°], elevation angle, height of the sun in the sky
z
Φ
*animation from pveducation

## Slide 19: Modeling steps
Weather data:
The sun path is characterized by:
z [°], elevation angle, height of the sun in the sky
Φ [°], the azimuth angle: angle of sun between north and sun direction
z
Φ
*animation from pveducation
*animation from pveducation

## Slide 20: Modeling steps
Weather data:
The sun path is characterized by:
z [°], elevation angle, height of the sun in the sky
Φ [°], the azimuth angle: angle between north and the sun direction
Φ [°]
z [°]
Typical sun path diagram

## Slide 21: Modeling steps
Weather data:
The sun path is characterized by:
z [°], elevation angle, height of the sun in the sky
Φ [°], the azimuth angle: angle between north and the sun direction
Remember ? To calculate BHI:
z
Φ
With , the zenith angle
the zenith angle
*image adapted from PVSC48 tutorial

## Slide 22: Modeling steps
2. Plan-of-Array Irradiance
Reminder, the Global Plane-Of-Array (GPOA) irradiance can be calculated from DHI, GHI and DNI.

## Slide 23: Modeling steps
2. Plan-of-Array Irradiance
Reminder, the Global Plane-Of-Array (GPOA) irradiance can be calculated from DHI, GHI and DNI and are broken down into 3 components:
Souza, Muriele et al. (2019). Determination of Diffused Irradiation from Horizontal Global Irradiation - Study for the City of Curitiba.
: The direct component - Power received from the Beam of the sun on the horizontal plan
: The ground-reflected component - Power received from reflections from the ground
: The diffuse component - Power received from the sky diffusion of the light,

## Slide 24: Modeling steps
Souza, Muriele et al. (2019). Determination of Diffused Irradiation from Horizontal Global Irradiation - Study for the City of Curitiba.
Under the isotropic/no-shading assumption
2. Plan-of-Array Irradiance
Reminder, the Global Plane-Of-Array (GPOA) irradiance can be calculated from DHI, GHI and DNI and are broken down into 3 components:
With:
, PV installation tilt

## Slide 25: Modeling steps
=
With:
AOI, angle of incidence
, PV installation tilt
, PV installation azimuth
Sun elevation
, sun azimuth
Under the isotropic/no-shading assumption
2. Plan-of-Array Irradiance
Reminder, the Global Plane-Of-Array (GPOA) irradiance can be calculated from DHI, GHI and DNI and are broken down into 3 components:

## Slide 26: Modeling steps
2. Plan-of-Array Irradiance
Use the notebook: https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy/blob/master/notebooks/python_intro_poa.ipynb
Follow the python tutorial and calculate the 3 POA components for:
One timestep
Over one year
Time for some hands-on exercises

## Slide 27: Modeling steps
3. Shading
Shadow can come from near and far elements and their impact can be distinguished into two categories
Partial shading refers to a condition where some but not all of the solar cells or panels in a PV array are exposed to sunlight while others are shaded.
Full shading occurs when the entire PV array is covered and deprived of direct sunlight.
*https://mcisolutions.ca/effect-of-shade-on-solar-panels/

## Slide 28: Modeling steps
Not treated in this course but, in average, if a PV panel is around 8% covered, the whole PV panel is bypassed and then, do not produce.
3. Shading
Shadow can come from near and far elements and their impact can be distinguished into two categories
Partial shading refers to a condition where some but not all of the solar cells or panels in a PV array are exposed to sunlight while others are shaded.
Full shading occurs when the entire PV array is covered and deprived of direct sunlight.
*https://mcisolutions.ca/effect-of-shade-on-solar-panels/
Demonstrated in one of pvlib example: https://pvlib-python.readthedocs.io/en/stable/gallery/shading/plot_partial_module_shading_simple.html

## Slide 29: Modeling steps
3. Shading
The Fisheye camera enables to account for the in-situ (full) shading in PV modeling.
Example in South of France
East
South
West
North
Fisheye camera

## Slide 30: Modeling steps
3. Shading
The Fisheye camera enables to account for the in-situ (full) shading in PV modeling.
Fisheye camera
Example in South of France
East
South
West
North

## Slide 31: Modeling steps
3. Shading
The Fisheye camera enables to account for the in-situ (full) shading in PV modeling.
Under the black curve, simple assumptions lead to:
are not significantly modified
Example in South of France
East
South
West
North

## Slide 32: Modeling steps
3. Soiling losses
Big subject in the PV industry:
Report of 130 pages on PV soiling: IEA PVPS, Soiling Losses – Impact on the Performance of Photovoltaic Power Plants 2022

## Slide 33: Modeling steps
3. Soiling losses
Can roughly be ignored in France according to the HSU model.
Model HSU: M. Coello and L. Boyle, "Simple Model for Predicting Time Series Soiling of Photovoltaic Panels, Sept. 2019.

## Slide 34: Modeling steps
3. Shading / Terrain horizon mask
Time for some hands-on exercises,
Again!

## Slide 35: Modeling steps
3. Shading / Terrain horizon mask
PVGIS: Website/Online Tool to estimate power production:
Enables to extract the horizon mask with a Digital Surface Model (DSM).
Go to: https://re.jrc.ec.europa.eu/pvg_tools/en/
Time for some hands-on exercises,
Again !

## Slide 36: Modeling steps
3. Shading / Terrain horizon mask
PVGIS: Website/Online Tool to estimate power production: https://re.jrc.ec.europa.eu/pvg_tools/en/
Enables to extract the horizon mask with a Digital Surface Model (DSM).
Instructions:
Generate a simulation on PVGIS
  Click on the map on Grenoble and select the « Grid connected tab »
  Vizualize
  Extract the horizon file in csv format
2. Follow the instructions on the jupyter notebook and calculate the modified POA on one year. https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy/blob/master/notebooks/python_intro2_horizon_mask.ipynb
Notes: Show function
Create function to get the API horizon mask
How many hours is the direct component blocked ?

## Slide 37: Resources
Modeling guide PVPMC: https://pvpmc.sandia.gov/modeling-guide/
Python / Pvlib tutorial: https://pvsc-python-tutorials.github.io/PVSC48-Python-Tutorial/
To go further:
  The Use of Advanced Algorithms in PV Failure Monitoring: https://iea-pvps.org/wp-content/uploads/2021/10/Final-Report-IEA-PVPS-T13-19_2021_PV-Failure-Monitoring.pdf

## Slide 38: Appendix
How to install Python and import the course repository to use the notebooks on your local PC.
Install python: www.python.org/downloads/, download and install the 3.9.13 “release” (Add python to your Path)
Go to https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy, click on the green “Code” button and then download the folder as the zip

## Slide 39: Appendix
How to install Python and import the course repository to use the notebooks on your local PC.
Install python: www.python.org/downloads/, download and install the 3.9.13 “release” (Add python to your Path)
Go to https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy, click on the green “Code” button and then download the folder as the zip
Unzip it and put it in adequate location in your PC.
Let’s create a virtual environment where you will find all the functions for this course:
  Go in the folder and open the command line from that same folder by writing “cmd” in the path bar (with Windows)

## Slide 40: Appendix
How to install Python and import the course repository to use the notebooks on your local PC.
Install python: www.python.org/downloads/, download and install the 3.9.13 “release” (Add python to your Path)
Go to https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy, click on the green “Code” button and then download the folder as the zip
Unzip it and put it in adequate location in your PC.
Let’s create a virtual environment where you will find all the functions for this course:
  Go in the folder and open the command line from that same folder by writing “cmd” in the path bar (with Windows)
  In the command bar: execute the following line to create the “solar_env” environnement that you will use in your notebooks
    “pip install virtualenv”
    “python –m virtualenv solar_env”
    “call solar_env\Scripts\activate” (you should have a ‘solar_env’ on the left of the command at this point)
    “pip install –r requirements.txt” (load all the libraries, take a little time, be patient)
    “python -m ipykernel install --name=solarkernel” (create a kernel for the notebooks)
It’s ready !

## Slide 41: Appendix
How to start a notebook
Go in the folder and open the command line from that same folder by writing “cmd” in the path bar (with Windows)
In the command bar, exexute:
  “call solar_env\Scripts\activate” (go in the virtual env)
  “jupyter notebook” (open the notebooks browser)
3. Browse to the notebooks folder, choose one and pick the solarkernel when asked.