## Slide 1
Operational research for urban solar development
“PV failure detection based on operational time series”
Alexandre Mathieu
09/12/2024

## Slide 2: Curriculum
Day | Time | Duration | Content
Wednesday 13/11/2024 | 11h15-12h45 14h15-15h45 | 1h30 + 1h30 | 50% Lecture / 50 % Hands-on
Tuesday 26/11/2024 | 9h45-13h00 | 1h30 + 1h30 | 25% Lecture / 75 % Hands-on
Monday 02/12/2024 | 13h15-16h15 | 3h | 15% Lecture / 85 % Hands-on
Monday 09/12/2024 | 8h-11h 13h15-16h15 | 6h | 10% Lecture / 90 % Hands-on/Project
Tuesday 10/12/2024 | 8h-11h | 3h | 10% Lecture / 90 % Project
Monday 16/12/2024 | 8-11h | 3h | 10% Lecture / 90 % Project
Thursday 19/12/2024 | 9h45-12h45 | 3h | 10% Lecture / 90 % Project
Monday 06/01/2025 | 13h15-14h45 | 1h30 | 100% Project
Monday 13/01/2025 | 9h45-11h45 | 1h30 | 100% Project
Total |  | 27h | 
Plan

## Slide 3: Agenda
Review notebook last week
PV performance model steps

## Slide 4: Agenda
Review notebook last week
PV performance model steps

## Slide 5: Review first notebook
Notebook recap 02/12/2024
Google collab link: https://colab.research.google.com/drive/1ncPYAOFvJvU_Tc5goPQL9F9wLNUh1FzQ?usp=sharing
Correction: https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy/blob/master/notebooks/ac_power_estimation.ipynb

## Slide 6: Modeling steps
Notebook recap 02/02/2024
Python commands
import matplotlib.pyplot as plt
!pip install pvlib # In google collab, download the pvlib package
# Make a figure with one axis
fig, ax = plt.subplots(1, 1, figsize=(9,6))
df.plot(ax=ax) # Plot df (pd.Series or pd.DataFrame) on the axis “ax”
# Make a figure with two axes (two figures top/bottom) which share the same x axis
fig, (ax1, ax2) = plt.subplots(2, 1, figsize=(9,6), sharex=True)
# Force values to be between 0 and 1 (any value lower than 0 will be changed to 0 and any value higher than 1 will be adjusted down to 1)
# “eta” must be a pd.Series or pd.DataFrame to apply the “.clip()” method
eta = eta.clip(lower=0, upper=1)
# Select all df values between two dates: 10/06/2020 & 15/06/2020 in this case
# The index must be “DateTime” index
df.loc["20200610":"20200615"]

## Slide 7: Agenda
Review notebook last week
PV performance model steps

## Slide 8: Modeling steps
5. Module and String IV Curve

## Slide 9: Modeling steps
5. Module and String IV Curve
For a fixed irradiance and module temperature, the PV module has its I, current which depends on V, voltage and it can take many operating points.

## Slide 10: Modeling steps
5. Module and String IV Curve
Equivalent-circuit model
IL
ID
I
V
+
-
Model 1 diode – 3 parameters
In parallel of the photocurrent that is generated according to the irradiance, the model:
- Assumes that the PV module acts as a diode

## Slide 11: Modeling steps
5. Module and String IV Curve
Equivalent-circuit model
Model 1 diode – 4 parameters
IL
ID
I
V
+
-
Rs
+
In parallel of the photocurrent that is generated according to the irradiance, the model:
- Assumes that the PV module acts as a diode
- Estimates the conduction losses
Rs slope corrected

## Slide 12: Modeling steps
5. Module and String IV Curve
Equivalent-circuit model
Model 1 diode – 5 parameters
IL
ID
I
V
+
-
Rs
+
IL
Rsh
Rsh slope corrected
In parallel of the photocurrent that is generated according to the irradiance, the model:
- Assumes that the PV module acts as a diode
- Estimates the conduction losses
- Estimates the leakage current (going through the module frame or others)
W. De Soto, S.A. Klein, W.A. Beckman, Improvement and validation of a model for photovoltaic array performance, Solar Energy, Volume 80, Issue 1, 2006

## Slide 13: Modeling steps
5. Module and String IV Curve
Les 5 parameters are the 5-parameters at conditions STC ( et
Then, the parameters at environmental conditions (G: POA irradiance, : Cell temperature) vary according to the following relationships It expects temperatures in Kelvin !
The photocurrent [A]
The reverse saturation current [A] -
The series resistance [Ω]
The product of the diode ideality factor, number of cells and cell thermal voltage [V]:
The shunt resistance [Ω]
The silicon energy band in [eV]
+
k, Boltzmann constant: 8,617 [eV/K]
W. De Soto, S.A. Klein, W.A. Beckman, Improvement and validation of a model for photovoltaic array performance, Solar Energy, Volume 80, Issue 1, 2006
IL
ID
I
V
+
-
Rs

## Slide 14: Modeling steps
5. Module and String IV Curve
Les 5 parameters enable to formulate for any environmental conditions.
+
W. De Soto, S.A. Klein, W.A. Beckman, Improvement and validation of a model for photovoltaic array performance, Solar Energy, Volume 80, Issue 1, 2006

## Slide 15: Modeling steps
5. Module and String IV Curve
Les 5 parameters enable to formulate
+
But… the equation resolution is not that direct:
With
W. De Soto, S.A. Klein, W.A. Beckman, Improvement and validation of a model for photovoltaic array performance, Solar Energy, Volume 80, Issue 1, 2006

## Slide 16: Modeling steps
5. Module and String IV Curve
Les 5 parameters enable to formulate
+
But… the equation resolution is not that direct:
With
W. De Soto, S.A. Klein, W.A. Beckman, Improvement and validation of a model for photovoltaic array performance, Solar Energy, Volume 80, Issue 1, 2006
https://pvlib-python.readthedocs.io/en/v0.11.1/reference/generated/pvlib.pvsystem.v_from_i.html#pvlib.pvsystem.v_from_i
Fortunately,

## Slide 17: Modeling steps
Reference Image: https://pvcase.com
5. Module and String IV Curve
Bypass diodes
Bypass diodes in PV modules are used to handle important mismatch cases such as shading, cell crack, uneven soiling, etc... to prevent significant losses at the module level and high reverse voltages which would induce hotspots at the cell level.
Those are typically Schottky diodes which are commonly 3 (between 2 and 5) per PV module, each in parallel of a group of around 20 cells.

## Slide 18: Modeling steps
Reference Image: https://pvcase.com
5. Module and String IV Curve
Bypass diodes
Bypass diodes in PV modules are used to handle important mismatch cases such as shading, cell crack, uneven soiling, etc... to prevent significant losses at the module level and high reverse voltages which would induce hotspots at the cell level.
Those are typically Schottky diodes which are commonly 3 (between 2 and 5) per PV module, each in parallel of a group of around 20 cells.
(Ideal) Diode effect:
Around -1.5 V
Limit negative voltages

## Slide 19: How can Machine Learning Tools enable better estimation and failure detection ?
Methods like Polynomial Regression, Decision Trees, and KNN deliver high accuracy when applied to sensible training datasets.

## Slide 20: How can Machine Learning Tools enable better estimation and failure detection ?
Methods like Polynomial Regression, Decision Trees, and KNN deliver high accuracy when applied to sensible training datasets.
PVWatts Model
Perfect use case for Regression techniques to optimize and to minimize errors effectively.

## Slide 21: How can Machine Learning Tools enable better estimation and failure detection ?
Methods like Polynomial Regression, Decision Trees, and KNN deliver high accuracy when applied to sensible training datasets.
PVWatts Model
Perfect use case for Regression techniques to optimize and to minimize errors effectively.
Importance of Residual Analysis:
Always analyze residuals (actual – model) values to:
  Identify biases using histograms or scatter plots.
  Understand model limitations.
  Add post-processing layers for error correction.
Residual histogram
Residual mainly contained between -500 W and 0W
Constant biais
Two/Three local peaks

## Slide 22: How can Machine Learning Tools enable better estimation and failure detection ?
Methods like Polynomial Regression, Decision Trees, and KNN deliver high accuracy when applied to sensible training datasets.
PVWatts Model
Perfect use case for Regression techniques to optimize and to minimize errors effectively.
Importance of Residual Analysis:
Always analyze residuals (actual – model) values to:
  Identify biases using histograms or scatter plots.
  Understand model limitations.
  Add post-processing layers for error correction.
Error Metrics :
Mean Error
Mean Absolute Error
​
Observed value at instance i.
​: Predicted value at instance i.
n: Total number of observations.

## Slide 23: Failure detection: Few insights

## Slide 24: Failure detection: Few insights
Threshold-Based Approach:
Sets predefined performance thresholds.
Failure Identification: Flags deviations when performance metrics (e.g., voltage, current) exceed the thresholds
Reference image: DNV

## Slide 25: Failure detection: Few insights
Threshold-Based Approach:
Sets predefined performance thresholds.
Failure Identification: Flags deviations when performance metrics (e.g., voltage, current) exceed the thresholds
Unsupervised Learning:
Detects anomalies by clustering or analyzing patterns without labeled data.
Common Techniques:
  K-Means Clustering
  Principal Component Analysis (PCA)
Reference image: DNV
Reference image: The Use of Advanced Algorithms in
PV Failure Monitoring 2021, IEA Report

## Slide 26: Modeling steps
Implement the 1-diode parameter model, improve the accuracy of DC power models and detect underperformances https://colab.research.google.com/drive/1ncPYAOFvJvU_Tc5goPQL9F9wLNUh1FzQ?usp=sharing
Time for some hands-on exercises !

## Slide 27: Agenda
PV « expected » losses

## Slide 28: Wooclap survey

## Slide 29: PV « expected » losses
Bun, L., 2011. Détection et localisation de défauts dans un système photovoltaïque (Theses). Université de Grenoble.
Module temperature losses
Non-optimal irradiance collection (light, reflection, known shading)
Non-optimal array production extraction (example: mismatch)
Natural system ageing
Joule losses in the cables
Inverter losses
Notes: - Non-optimal extraction of energy production: mismatch between modules in terms of nominal power, which induces imbalances, and very generally, the operational system adapts to the weakest module.
- Losses by temperature: + It is hot, - the module is efficient. Example (order of magnitude) on a crystal module, a temperature rise of 30° corresponds to a loss of 10%
Collection of non-optimal irradiance: Effects of reflection, spectral and shading due to elements surrounding the installation
Losses due to aging: Natural loss: encapsulant which turns brown, micro cracks in the cells, resistance of the wiring which increases…
Losses in cables due to resistance. Efficiency losses in the conversion between DC and AC.

## Slide 30: Agenda
PV Failure

## Slide 31: PV failure definition
Inspired from the IEA definition*, a failure occurs when**:
the system power measured according to IEC 60904
the total uncertainty of the measurement
the expected system power
the expected system power tolerance
In other words, a failure is an underperformance which is not planned at the design phase.
*M. Köntges et al., “Review of Failures of Photovoltaic Modules,” IEA PVPS T13, IEA-PVPS T13-01:2014, 2014.
***A. Mathieu, G. Fraisse, M. Thebault, S. Thebault, S. Boddaert, and L. Gaillard, ‘Failure Risk Analysis of Photovoltaic Systems Based on Literature Review’, presented at the Eurosun 2022, Kassel, Germany, Sep. 2022.

## Slide 32: PV failure definition
Inspired from the IEA definition*, a failure occurs when**:
the system power measured according to IEC 60904
the total uncertainty of the measurement
the expected system power
the expected system power tolerance
In other words, a failure is an underperformance which is not planned at the design phase.
*M. Köntges et al., “Review of Failures of Photovoltaic Modules,” IEA PVPS T13, IEA-PVPS T13-01:2014, 2014.
***A. Mathieu, G. Fraisse, M. Thebault, S. Thebault, S. Boddaert, and L. Gaillard, ‘Failure Risk Analysis of Photovoltaic Systems Based on Literature Review’, presented at the Eurosun 2022, Kassel, Germany, Sep. 2022.

## Slide 33: Failures
One list of failures… Total: 26
*A. Mathieu, G. Fraisse, M. Thebault, S. Thebault, S. Boddaert, and L. Gaillard, ‘Failure Risk Analysis of Photovoltaic Systems Based on Literature Review’, presented at the Eurosun 2022, Kassel, Germany, Sep. 2022.

## Slide 34: Failures
One list of failures… Total: 26
*A. Mathieu, G. Fraisse, M. Thebault, S. Thebault, S. Boddaert, and L. Gaillard, ‘Failure Risk Analysis of Photovoltaic Systems Based on Literature Review’, presented at the Eurosun 2022, Kassel, Germany, Sep. 2022.
derating

## Slide 35: Failures
One list of failure…
*A. Mathieu, G. Fraisse, M. Thebault, S. Thebault, S. Boddaert, and L. Gaillard, ‘Failure Risk Analysis of Photovoltaic Systems Based on Literature Review’, presented at the Eurosun 2022, Kassel, Germany, Sep. 2022.
The 12 most critical according to *
derating

## Slide 36: Agenda
Common PV Failures

## Slide 37: Inverter defect
The inverter is often responsible for most of the maintenance events. Several failures can occur over the inverter lifespan due to unexpected events or aging mechanisms.
The most common failures in the inverter due to aging come from components such as the relays, the capacitors, the semiconductor modules (IGBT and diodes), cooling fan, and the printed circuit board.
Software issues or a lack of restart after an event can also shut down the inverter and can be solved by rebooting the software or updating the firmware.
Detection Hints:
Abrupt performance drop from a specific date.
Complete shutdown: Produces 0 W.
K. Sinclair, M. Sinclair, "Silicon solar module visual inspection guide: Catalogue of Defects to be used as a Screening Tool

## Slide 38: Inverter clipping
« Inverter clipping » occurs when the generated DC power exceeds the inverter limit.
Then, the inverter caps the generated DC power by moving the operating point to reduce the DC production and fit within the inverter input limits.

## Slide 39: Inverter clipping
« Inverter clipping » occurs when the generated DC power exceeds the inverter limit.
Then, the inverter caps the generated DC power by moving the operating point to reduce the DC production and fit within the inverter input limits.
Example where the inverter increases the tension to reduce the DC power.

## Slide 40: Inverter clipping
« Inverter clipping » occurs when the generated DC power exceeds the inverter limit.
Then, the inverter caps the generated DC power by moving the operating point to reduce the DC production and fit within the inverter input limits.
Example where the inverter increases the tension to reduce the DC power.
Signature

## Slide 41: Inverter clipping
« Inverter clipping » occurs when the generated DC power exceeds the inverter limit.
Then, the inverter caps the generated DC power by moving the operating point to reduce the DC production and fit within the inverter input limits.
Example where the inverter increases the tension to reduce the DC power.
Detection Hints:
Clipping threshold is generally fixed.
Occurs at high sunny conditions.
Power Slope = 0 W/m2/h.
Slight increase of voltage compared to standard operation.
Current loss.
Signature

## Slide 42: Cable/Connector defect: Open-circuited string
Wiring defect might lead to fire.
DC cable failure can occur due to various reasons at different phases.
At the design phase, cables which are incorrectly dimensionned may result in overheating and early cable degradation.
During the installation, pinching or pulled cables can also lead to early defects.
DC cables might also deteriorate faster or might corrode if exposed to harsh environments such as UV radiation, rodents, or birds.
Connector failures come typically from forcing different types of connectors to connect or not-well crimped connectors.
Even if aging mechanisms with corrosion due to long exposure to weather with UV and humidity are identified for connectors, failures are most likely to be related to installation issues.
Images. M. Köntges et al. , Review of Failures of Photovoltaic Modules, Report IEA-PVPS T13-01: ISBN 978-3-906042-16-9, 2014.
Detection Hints:
Abrupt performance change from a specific date
The voltage is not expected to vary.
Loss of current proportional to the number of strings which an open-circuited.

## Slide 43: Shading
Shading refers to the obstruction of sunlight on the PV array.

## Slide 44: Shading / Full shading
Shading refers to the obstruction of sunlight on the PV array.
One example
Image: “Measuring sky view factor of urban canyons using hacked Gopro hemispheric video processing”, December 2015, Conference, Melbourne, Australia, White et Kimm

## Slide 45: Shading / Full shading
*Process illustration, assumptions made on the building masks.
Shading refers to the obstruction of sunlight on the PV array.
One example
Image: “Measuring sky view factor of urban canyons using hacked Gopro hemispheric video processing”, December 2015, Conference, Melbourne, Australia, White et Kimm

## Slide 46
*Process illustration, assumptions made on the building masks.
Image: “Measuring sky view factor of urban canyons using hacked Gopro hemispheric video processing”, December 2015, Conference, Melbourne, Australia, White et Kimm
Shading refers to the obstruction of sunlight on the PV array.
One example
Shading / Full shading
Signature

## Slide 47: Shading / Full shading
*Process illustration, assumptions made on the building masks.
Detection Hints:
Temporal cycle
Correlated with the sun position (Low sun horizons have higher chances to result in shading.)
Power/Current decrease in the same order of magnitude as the POA-direct component vs POA-global
Sudden drops/increase
Shading refers to the obstruction of sunlight on the PV array.
One example
Image: “Measuring sky view factor of urban canyons using hacked Gopro hemispheric video processing”, December 2015, Conference, Melbourne, Australia, White et Kimm
Signature

## Slide 48: Bypass short-circuit
Diode failures can appear at different stages:
Manufacturing: wrong specification, non-functional diode..
Installation: Wrong installation (inversed or not properly connected),mechanical stress on junction boxes, shocks. . .
Operation: Diode aging mechanisms, junction box corrosion, events with mechanical stresses, repetive activation (partial shadings).
Failed diodes are either blocked in short-circuit or open-circuit.
Detection Hints:
Short-circuited bypass diodes constantly lower the module voltage by around 1/3 if there are 3 diodes in the module.
Abrupt performance change from a specific date
Image reference: Romenia G. Vieira et al. “A Comprehensive Review on Bypass Diode Application on Photovoltaic Modules”. In:Energies13.10 (2020)

## Slide 49
That’s it