## Slide 1
Operational research for urban solar development
“PV failure detection based on operational time series”
Alexandre Mathieu
05/12/2023 - Morning

## Slide 2: Agenda
Curriculum
PV performance model steps

## Slide 3: Curriculum
Day | Time | Duration | Content
Monday 27/11/2023 | 9h45-11h15 12h30-14h | 1h30 + 1h30 | 50% Lecture / 50 % Hands-on
Tuesday 05/12/2023 | 8h-9h30 9h45-11h15 | 1h30 + 1h30 | 50% Lecture / 50 % Hands-on
Thursday 07/12/2023 | 8h-11h 12h45-15h45 | 6h | 25% Lecture / 75 % Project
Monday 11/11/2023 | 8h-11h 12h30-15h30 | 6h | 10% Lecture / 90 % Project
Friday 22/12/2023 | 8h-9h30 | 1h30 | 100 % Project
Plan
Today

## Slide 4: Curriculum
Day | Time | Duration | Content
Monday 27/11/2023 | 9h45-11h15 12h30-14h | 1h30 + 1h30 | 50% Lecture / 50 % Hands-on
Tuesday 05/12/2023 | 8h-9h30 9h45-11h15 | 1h30 + 1h30 | 50% Lecture / 50 % Hands-on
Thursday 07/12/2023 | 8h-11h 12h45-15h45 | 6h | 25% Lecture / 75 % Project
Monday 11/11/2023 | 8h-11h 12h30-15h30 | 6h | 10% Lecture / 90 % Project
Friday 22/12/2023 | 8h-9h30 | 1h30 | 100 % Project
Plan
For next time. Make groups of 2 for the project.
Today

## Slide 5: Agenda
Curriculum
PV performance model steps

## Slide 6: Modeling steps
*image from: PVSC48 python tutorial
27/11/2023

## Slide 7: Modeling steps
*image from: PVSC48 python tutorial
27/11/2023
Today

## Slide 8: Modeling steps
Notebook recap 27/11/2023
The notebook is now corrected and can be read online: https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy/blob/master/notebooks/python_intro_poa.ipynb

## Slide 9: Modeling steps
Notebook recap 27/11/2023
Python commands 1/2
import numpy as np # import to your python instance the package “numpy” and rename it “np” (helpful for math calculations)
import pandas as pd # import to your python instance the package “pandas” (helpful for data structure and calculations)
ts = pd.Series([1, 2,3], index=['a','b','c']) # Initiate a pandas serie into variable “ts”
ts2 = ts + ts/2 + np.cos(ts) + np.pi # Make calculate with “ts” and store it into “ts2”
print(ts2) # print serie ts
ts.plot(marker="o") # Make a plot of ts with “o” (circle) marker
df = pd.DataFrame() # Initiate an empty dataframe into variable “df”
df["first_column"] = ts # Store “ts” serie in a column labeled “first_column”
df["second_column"] = ts2 * 2 # Store “ts2” serie in another column labeled “second_column”
df.plot(marker="o") # Make a plot of df with “o” (circle) marker
df.loc[“a”, :] # Select the entire row with “a” as index
df.loc[“a”, “first_column”] # Select the value with “a” as index and “first_column” as column
a | 1
b | 2
c | 3
index
values
ts
a | 1 | 2
b | 2 | 4
c | 3 | 6
df
Pvlib ref *William F. Holmgren, Clifford W. Hansen, and Mark A. Mikofski. “pvlib python: a python package for modeling solar energy systems.” Journal of Open Source Software, 3(29), 884, (2018). https://doi.org/10.21105/joss.00884
index

## Slide 10: Modeling steps
Notebook recap 27/11/2023
Python commands 2/2
####### Calculate POA, the lazy way #######
from pvlib.irradiance import get_total_irradiance # import the function “get_total_irradiance from pvlib”
# On another note, pvlib* is a very useful package for PV modeling with plenty of convenient functions, do not hesitate to look it up on the web
beta = 20 # tilt [°]
azimuth = 180 # azimuth [°]
rho = 0.2 # albedo
solar_position = pd.read_csv("solarpos_data.csv") # Import the data file "solarpos_data.csv“ which contains the sun path (azimuth and elevation) with datetime index
weather_data = pd.read_csv(DATA_PATH / "sat_data.csv", index_col=0) # Import the data file “sat_data.csv“ which irradiance (dni, ghi, dhi) with datetime index
data = get_total_irradiance(beta, azimuth, solar_position["zenith"], solar_position["azimuth"], weather_data["dni"], weather_data["ghi"], weather_data["dhi"], albedo=rho) # Directly apply the isotropic models
print(data.head(24)) # Show the first 24 lines of the DataFrame
values
Pvlib ref *William F. Holmgren, Clifford W. Hansen, and Mark A. Mikofski. “pvlib python: a python package for modeling solar energy systems.” Journal of Open Source Software, 3(29), 884, (2018). https://doi.org/10.21105/joss.00884

## Slide 11: Modeling steps
3. Shading / Terrain horizon mask
PVGIS: Website/Online Tool to estimate power production:
Enables to extract the horizon mask with a Digital Surface Model (DSM).
Go to: https://re.jrc.ec.europa.eu/pvg_tools/en/
Time for some hands-on exercises,
Again !

## Slide 12: Modeling steps
3. Shading / Terrain horizon mask
PVGIS: Website/Online Tool to estimate power production: https://re.jrc.ec.europa.eu/pvg_tools/en/
Enables to extract the horizon mask with a Digital Surface Model (DSM).
Instructions:
Generate a simulation on PVGIS
  Click on the map on Grenoble and select the « Grid connected tab »
  Vizualize
  Extract the horizon file in csv format
2. Follow the instructions on the jupyter notebook and calculate the modified POA on one year. https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy/blob/master/notebooks/python_intro2_horizon_mask.ipynb
Notes: Show function
Create function to get the API horizon mask
How many hours is the direct component blocked ?

## Slide 13: Modeling steps
4. Module and Cell temperature
The hotter a module is, the less efficient it is !

## Slide 14: Modeling steps
4. Cell temperature
Ross model: Model to estimate the cell temperature [°C] as function of ambient temperature and irradiance [W/m²].
, typically in the range 0.02-0.05 K/m²/W.
Ross, R. G. Jr., (1981). “Design Techniques for Flat-Plate Photovoltaic Arrays”

## Slide 15: Modeling steps
4. Cell temperature
Ross model: Model to estimate the cell temperature [°C] as function of ambient temperature and irradiance [W/m²].
, typically in the range 0.02-0.05 K/m²/W.
can be fitted from datasheet values. NOCT conditions: = 800 W/m²
= 20°C
Ross, R. G. Jr., (1981). “Design Techniques for Flat-Plate Photovoltaic Arrays”

## Slide 16: Modeling steps
4. Cell temperature
Faiman model: Model to estimate the cell temperature [°C] as function of ambient temperature and irradiance [W/m²] AND wind .
Faiman, D. (2008). Assessing the outdoor operating temperature of photovoltaic modules.

## Slide 17: Modeling steps
4. Cell temperature
Faiman model: Model to estimate the cell temperature [°C] as function of ambient temperature and irradiance [W/m²] AND wind .
In some cases, can be assumed Between , only few degrees of difference
Faiman, D. (2008). Assessing the outdoor operating temperature of photovoltaic modules.

## Slide 18: Modeling steps
4. Cell temperature
Use the following notebook: https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy/blob/master/notebooks/dc_power_estimation.ipynb
Follow the python tutorial and estimate the cell temperature for one year.
Time for some hands-on exercises !

## Slide 19: Modeling steps
5. Module and String IV Curve

## Slide 20: Modeling steps
5. Module and String IV Curve
For a fixed irradiance and module temperature, the PV module has its I, current which depends on V, voltage and it can take many operating points.

## Slide 21: Modeling steps
In reality, the IV characteristics go out of the 1st quadrant and the module can potentially consume power.
5. Module and String IV Curve
For a fixed irradiance and module temperature, the PV module has its I, current which depends on V, voltage and it can take many operating points.

## Slide 22: Modeling steps
5. Module and String IV Curve
For a fixed irradiance and module temperature, the PV module has its I, current which depends on V, voltage and it can take many operating points
Then, the inverter is constantly searching for the operating point which maximizes the power MPP: Maximum Power Point.

## Slide 23: Modeling steps
5. Module and String IV Curve
For a fixed irradiance and module temperature, the PV module has its I, current which depends on V, voltage and it can take many operating points.
Then, the inverter is constantly searching for the operating. point which maximizes the power MPP: Maximum Power Point.
Especially, it changes the voltage with the MPP-Tracker (MPPT) to maximize power.

## Slide 24: Modeling steps
5. Module and String IV Curve
By the way… the IV curves can be summed up when the modules are connected in series or parallel! The inverter, then, maximizes the power of the PV array IV curve.
Bun, L.. “Détection et localisation de défauts pour un système PV.” (2011).

## Slide 25: Modeling steps
5. Module and String IV Curve
The IV curves' dependencies:
Higher cell temperatures mostly decrease the voltage
Higher irradiance level mostly increase the current
Example of I-V curves as function of different module temperature
Example of I-V curves as function of different irradiances

## Slide 26: Modeling steps
6. DC & Mismatch Losses
Not the focus of this class. However, keep in mind that:
DC wiring losses are around 0.5%-2%.
Mismatch losses refer to the fact that PV modules have different IV curves and this can entail significant losses.

## Slide 27: Modeling steps
6. DC & Mismatch Losses
Not the focus of this class. However, keep in mind that:
DC wiring losses are around between 0.5% and 2%.
Mismatch losses refers to the fact that PV modules have different IV curves and this can entail significant losses. For instance, if one of them has a very degraded IV curve (shading or other), it can significantly degrade the IV curve at the array level.
Bun, L.. “Détection et localisation de défauts pour un système PV.” (2011).

## Slide 28: Modeling steps
5./6./7. Power model
Constant efficiency model:
With:
, DC power in [W]
efficiency around 20% (from datasheet)
the irradiance in the plane of array [W/m²]
, the PV installation area [m2]

## Slide 29: Modeling steps
5./6./7. Power model
Constant efficiency model:
With:
, DC power in [W]
efficiency around 20% (from datasheet)
the irradiance in the plane of array [W/m²]
, the PV installation area [m2]
Not really precise for instantaneous values

## Slide 30: Modeling steps
5./6./7. Power model
The PVWatts power model enables to take into account the effect of the cell temperature
With:
Nominal DC power
the irradiance in the plane of array [W/m²]
(negative, usually between -0.2 – -0.5 % W/m²/°C)
, the cell temperature [°C]
PVWatts model: A. P. Dobos, “PVWatts Version 5 Manual” (2014).

## Slide 31: Modeling steps
5./6./7. Power model
The Huld model (used in PVGIS) enables to take into account the module temperature and non-lineary with irradiance.
With:
, the reference efficiency (around 20%) [%]
the irradiance in the plane of array [W/m²]
, the PV installation area [m2]
the normalized irradiance
, the module temperature delta [°C]
coefficients
Huld model: Thomas Huld et al., A power-rating model for crystalline silicon PV modules, 2011,

## Slide 32: Modeling steps
5./6./7. Power model
The Huld model (used in PVGIS) enables to take into account the module temperature and non-lineary with irradiance.
With:
, the reference efficiency (around 20%) [%]
the irradiance in the plane of array [W/m²]
, the PV installation area [m2]
the normalized irradiance
, the module temperature delta [°C]
coefficients
Reference values from PVGIS
Huld model: Thomas Huld et al., A power-rating model for crystalline silicon PV modules, 2011,

## Slide 33: Modeling steps
8. Inverter model
The PVWatts inverter model enables to calculate a generic AC/DC efficiency
With:
PVWatts model: A. P. Dobos, “PVWatts Version 5 Manual” (2014).

## Slide 34: Modeling steps
8. Inverter model
The Sandia inverter model enables to include the voltage and be more precise
Where:
D. King, S. Gonzalez, G. Galbraith, W. Boyson, “Performance Model for Grid-Connected Photovoltaic Inverters”, SAND2007-5036, Sandia National Laboratories
Parameters:
DC input voltage (V). This is typically assumed to be the array’s maximum power voltage.
: DC voltage level (V) at which the AC power rating is achieved at reference operating conditions.
: AC output power (W)
: Maximum AC power rating for inverter at reference conditions (W). Assumed to be an upper limit.
: DC power level (W) at which the AC power rating is achieved at reference operating conditions.
: DC power required to start the inversion process (W)
,, : Empirical coefficients

## Slide 35: Modeling steps
5./6./7. Power model
Use the following notebook: https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy/blob/master/notebooks/dc_power_estimation.ipynb
Follow the python tutorial and estimate the DC power for one year.
Time for some hands-on exercises !

## Slide 36: Resources
Modeling guide PVPMC: https://pvpmc.sandia.gov/modeling-guide/
Python / Pvlib tutorial: https://pvsc-python-tutorials.github.io/PVSC48-Python-Tutorial/
To go further:
  The Use of Advanced Algorithms in PV Failure Monitoring: https://iea-pvps.org/wp-content/uploads/2021/10/Final-Report-IEA-PVPS-T13-19_2021_PV-Failure-Monitoring.pdf

## Slide 37: Appendix
How to install Python and import the course repository to use the notebooks on your local PC.
Install python: www.python.org/downloads/, download and install the 3.9.13 “release” (Add python to your Path)
Go to https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy, click on the green “Code” button and then download the folder as the zip

## Slide 38: Appendix
How to install Python and import the course repository to use the notebooks on your local PC.
Install python: www.python.org/downloads/, download and install the 3.9.13 “release” (Add python to your Path)
Go to https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy, click on the green “Code” button and then download the folder as the zip
Unzip it and put it in adequate location in your PC.
Let’s create a virtual environment where you will find all the functions for this course:
  Go in the folder and open the command line from that same folder by writing “cmd” in the path bar (with Windows)

## Slide 39: Appendix
How to install Python and import the course repository to use the notebooks on your local PC.
Install python: www.python.org/downloads/, download and install the 3.9.13 “release” (Add python to your Path)
Go to https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy, click on the green “Code” button and then download the folder as the zip
Unzip it and put it in adequate location in your PC.
Let’s create a virtual environment where you will find all the functions for this course:
  Go in the folder and open the command line from that same folder by writing “cmd” in the path bar (with Windows)
  In the command bar: execute the following line to create the “solar_env” environnement that you will use in your notebooks
    “pip install virtualenv”
    “python –m virtualenv solar_env”
    “call solar_env\Scripts\activate” (you should have a ‘solar_env’ on the left of the command at this point)
    “pip install –r requirements.txt” (load all the libraries, take a little time, be patient)
    “python -m ipykernel install --name=solarkernel” (create a kernel for the notebooks)
It’s ready !

## Slide 40: Appendix
How to start a notebook
Go in the folder and open the command line from that same folder by writing “cmd” in the path bar (with Windows)
In the command bar, exexute:
  “call solar_env\Scripts\activate” (go in the virtual env)
  “jupyter notebook” (open the notebooks browser)
3. Browse to the notebooks folder, choose one and pick the solarkernel when asked.