## Slide 1
Operational research for urban solar development
“PV failure detection based on operational time series”
Alexandre Mathieu
02/12/2024

## Slide 2: Curriculum
Day | Time | Duration | Content
Wednesday 13/11/2024 | 11h15-12h45 14h15-15h45 | 1h30 + 1h30 | 50% Lecture / 50 % Hands-on
Tuesday 26/11/2024 | 9h45-13h00 | 1h30 + 1h30 | 25% Lecture / 75 % Hands-on
Monday 02/12/2024 | 13h15-16h15 | 3h | 15% Lecture / 85 % Hands-on
Monday 09/12/2024 | 8h-11h 13h15-16h15 | 6h | 10% Lecture / 90 % Hands-on/Project
Tuesday 10/12/2024 | 8h-11h | 3h | 10% Lecture / 90 % Project
Monday 16/12/2024 | 8-11h | 3h | 10% Lecture / 90 % Project
Thursday 19/12/2024 | 9h45-12h45 | 3h | 10% Lecture / 90 % Project
Monday 06/01/2025 | 13h15-14h45 | 1h30 | 100% Project
Monday 13/01/2025 | 9h45-11h45 | 1h30 | 100% Project
Total |  | 27h | 
Plan

## Slide 3: Agenda
Review notebook last week
PV performance model steps

## Slide 4: Agenda
Review notebook last week
PV performance model steps

## Slide 5: Review first notebook
Notebook recap 26/11/2024
Google collab link: https://colab.research.google.com/drive/1hB1pmBw-n7RiS99vCHQi2OKicfcQxpcO?usp=sharing
Correction: https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy/blob/master/notebooks/python_intro2_horizon_mask.ipynb

## Slide 6: Modeling steps
Notebook recap 26/11/2024
Python commands
import matplotlib.pyplot as plt
# Apply filters
filter_1 = weather_data["ghi"] > 800
filter_2 = (weather_data.index > pd.to_datetime("20220701").tz_localize("CET"))
filter = (filter_1) & (filter_2) # Combine with a “and” condition
weather_data.loc[filter, "dhi"] # Select only the rows which fulfills the filter condition
and show the DHI column from weather_data
# If statement
a=1
if a<0: # assertion: is "a" under 0 ? Do not forget the “:” at the end of the line
print("a is lower than 0") # Line non-executed since the assertion above is wrong, do not forget the “tab” indentation after a “if”
# Loop over all elements of a list or pd.Series which allow to perform task on each of the element
For element in [“a”,”b”]:
print(element)
for index, row in df.iterrows(): # Loop over all rows and index of the dataframe one by one
print(row["column1"] + row["column2"])
# Plot with matplotlib plt.plot(x, y, linewidth=0, marker="o") # scatter plot with no line in that case

## Slide 7: Agenda
Review notebook last week
PV performance model steps

## Slide 8: Modeling steps
4. Module and Cell temperature
The hotter a module is, the less efficient it is !

## Slide 9: Modeling steps
4. Cell temperature
Ross model: Model to estimate the cell temperature [°C] as function of ambient temperature and irradiance [W/m²].
, typically in the range 0.02-0.05 K/m²/W.
Ross, R. G. Jr., (1981). “Design Techniques for Flat-Plate Photovoltaic Arrays”

## Slide 10: Modeling steps
4. Cell temperature
Ross model: Model to estimate the cell temperature [°C] as function of ambient temperature and irradiance [W/m²].
, typically in the range 0.02-0.05 K/m²/W.
can be fitted from datasheet values. NOCT conditions: = 800 W/m²
= 20°C
Ross, R. G. Jr., (1981). “Design Techniques for Flat-Plate Photovoltaic Arrays”

## Slide 11: Modeling steps
4. Cell temperature
Faiman model: Model to estimate the module temperature [°C] as function of ambient temperature and irradiance [W/m²] AND wind .
Faiman, D. (2008). Assessing the outdoor operating temperature of photovoltaic modules.

## Slide 12: Modeling steps
4. Cell temperature
Faiman model: Model to estimate the module temperature [°C] as function of ambient temperature and irradiance [W/m²] AND wind .
In some cases, can be assumed Between , only few degrees of difference
Faiman, D. (2008). Assessing the outdoor operating temperature of photovoltaic modules.

## Slide 13: Modeling steps
5. Module and String IV Curve

## Slide 14: Modeling steps
5. Module and String IV Curve
For a fixed irradiance and module temperature, the PV module has its I, current which depends on V, voltage and it can take many operating points.

## Slide 15: Modeling steps
In reality, the IV characteristics go out of the 1st quadrant and the module can potentially consume power.
5. Module and String IV Curve
For a fixed irradiance and module temperature, the PV module has its I, current which depends on V, voltage and it can take many operating points.

## Slide 16: Modeling steps
5. Module and String IV Curve
For a fixed irradiance and module temperature, the PV module has its I, current which depends on V, voltage and it can take many operating points.
Then, the inverter is constantly searching for the operating point which maximizes the power MPP: Maximum Power Point.

## Slide 17: Modeling steps
5. Module and String IV Curve
For a fixed irradiance and module temperature, the PV module has its I, current which depends on V, voltage and it can take many operating points.
Then, the inverter is constantly searching for the operating point which maximizes the power MPP: Maximum Power Point.
Especially, it changes the voltage with the MPP-Tracker (MPPT) to maximize power.

## Slide 18: Modeling steps
5. Module and String IV Curve
By the way… the IV curves can be summed up when the modules are connected in series or parallel! The inverter, then, maximizes the power of the PV array IV curve.
Bun, L.. “Détection et localisation de défauts pour un système PV.” (2011).

## Slide 19: Modeling steps
5. Module and String IV Curve
The IV curves' dependencies:
Higher cell temperatures mostly decrease the voltage
Higher irradiance level mostly increase the current
Example of I-V curves as function of different module temperature
Example of I-V curves as function of different irradiances

## Slide 20: Modeling steps
6. DC & Mismatch Losses
Not the focus of this class. However, keep in mind that:
DC wiring losses are around 0.5%-2%.
Mismatch losses refers to the fact that PV modules have different IV curves and this can entail significant losses.

## Slide 21: Modeling steps
6. DC & Mismatch Losses
Not the focus of this class. However, keep in mind that:
DC wiring losses are around 0.5%-2%.
Mismatch losses refers to the fact that PV modules have different IV curves and this can entail significant losses. For instance, if one of them has a very degraded IV curve (shading or other), it can significantly degrade the IV curve at the array level.
Bun, L.. “Détection et localisation de défauts pour un système PV.” (2011).

## Slide 22: Modeling steps
5./6./7. Power model
Constant efficiency model:
With:
, DC power in [W]
efficiency around 20% (from datasheet)
the irradiance in the plane of array [W/m²]
, the PV installation area [m2]

## Slide 23: Modeling steps
Not really precise for instantaneous values
5./6./7. Power model
Constant efficiency model:
With:
, DC power in [W]
efficiency around 20% (from datasheet)
the irradiance in the plane of array [W/m²]
, the PV installation area [m2]

## Slide 24: Modeling steps
5./6./7. Power model
The PVWatts power model enables to take into account the effect of the cell temperature
With:
Nominal DC power [Wp] (installed capacity)
the irradiance in the plane of array [W/m²]
(negative, usually between -0.2 – -0.5 %/°C)
, the cell temperature [°C]
PVWatts model: A. P. Dobos, “PVWatts Version 5 Manual” (2014).

## Slide 25: Modeling steps
Huld model: Thomas Huld et al., A power-rating model for crystalline silicon PV modules, 2011,
5./6./7. Power model
The Huld model (used in PVGIS) enables to take into account the module temperature and non-lineary with irradiance.
With:
Nominal DC power [Wp] (installed capacity)
the irradiance in the plane of array [W/m²]
the normalized irradiance
, the module temperature delta [°C]
coefficients

## Slide 26: Modeling steps
Huld model: Thomas Huld et al., A power-rating model for crystalline silicon PV modules, 2011,
5./6./7. Power model
The Huld model (used in PVGIS) enables to take into account the module temperature and non-lineary with irradiance.
With:
Nominal DC power [Wp] (installed capacity)
the irradiance in the plane of array [W/m²]
the normalized irradiance
, the module temperature delta [°C]
coefficients
PVGIS coefficients

## Slide 27: Modeling steps
8. Inverter model
The PVWatts inverter model enables to calculate a generic AC/DC efficiency
With:
, by default 96%
PVWatts model: A. P. Dobos, “PVWatts Version 5 Manual” (2014).

## Slide 28: Modeling steps
8. Inverter model
The Sandia inverter model enables to include the voltage and be more precise
Where:
D. King, S. Gonzalez, G. Galbraith, W. Boyson, “Performance Model for Grid-Connected Photovoltaic Inverters”, SAND2007-5036, Sandia National Laboratories
Parameters:
DC input voltage (V).
: DC voltage level (V) at which the AC power rating is achieved
: AC output power (W)
: Maximum AC power rating for inverter at reference conditions (W).
: DC power level (W) at which the AC power rating is achieved.
: DC power required to start the inversion process (W)
,, : Empirical coefficients

## Slide 29: Modeling steps
10. Performance Metrics
Performance Ratio PR (IEC 61724 ): To calculate real performance
Real efficiency normalized by the efficiency in STC conditions STC: Standard Test Conditions (1000 W/m2, cell temperature of 25 °C, and AM1.5 spectrum)
With:
: Energy produced [Wh] over the period of time T
: Irradiation received [Wh/m²] over the period of time T
: Installation DC rated power [Wp]
, reference irradiation

## Slide 30: Modeling steps
10. Performance Metrics
Performance Ratio PR (IEC 61724 ): To calculate real performance
Real efficiency normalized by the efficiency in STC conditions STC: Standard Test Conditions (1000 W/m2, cell temperature of 25 °C, and AM1.5 spectrum)
With:
: Energy produced [Wh] over the period of time T
: Irradiation received [Wh/m²] over the period of time T
: Installation DC rated power [Wp]
, reference irradiation
Energy Performance Index EPI:
To monitor performance
𝑷𝑹 divided by expected (modelled)

## Slide 31: Modeling steps
Use the following notebook: https://github.com/AlexandreHugoMathieu/pvfault_detection_solar_academy/blob/master/notebooks/dc_power_estimation.ipynb
Follow the python tutorial and estimate the AC power for one year.
Time for some hands-on exercises !

## Slide 32
That’s it